## FORM
MODULE TYPE:
(USE 5 FOR MICROS)
| INVERTER 1 | INVERTER 2 | INVERTER 3 | INVERTER 4 | INVERTER 5
INVERTER MODEL:
# OF STRINGS:
# OF MODULES ON LARGEST STRING: (IF SOLAR EDGE W/ 3 STINGS, 2 OF:)
# OF MODULES ON ADDITIONAL STRING (ONLY IF DIFFERENT THAN LARGEST STRING): (IF SOLAR EDGE W/ 3 STRINGS, 1 OF:)
MODULE COUNT: | 0 |  |  | # OF MICROINVERTERS:
JOB NAME: |  |  | LINE TAPS OR BREAKER:
ADDRESS: |  |  | STATE?:
DATE: |  |  | INVERTER/SUBPANEL OUTSIDE?: | YES
DEAL: |  |  | HOW MANY MODULES ARE LANDSCAPED?: |  |  | PEAK TO GROUND: |  | FEET
SERVICE AMPERAGE: |  |  | ROOF MOUNT OR GROUND MOUNT?: | ROOF MOUNT |  |  |  | INCHES
TRINITY ACCOUNT #: |  |  | TRENCH?: | NO |  | R1 ORIENTATION: |  | °
MONITORING: | [5 empty] | PITCH: |  | °
UTILITY COMPANY: | [5 empty] | R2 ORIENTATION: |  | °
UTILITY ACCOUNT #: |  |  | # OF PIPES/VENTS BEING RELOCATED OR REMOVED: |  |  | PITCH: |  | °
UTILITY METER #: |  |  | BACKFEED BREAKER TYPE: |  |  | R3 ORIENTATION: |  | °
RACKING: |  |  | IS JOB CLOSE TO SALT WATER?: |  |  | PITCH: |  | °
DRAWER'S INITIALS: |  |  | STANDARD SHEATHING?: | YES |  | R4 ORIENTATION: |  | °
# OF ARRAYS: |  |  |  | ISSUED/REVISIONS |  | PITCH: |  | °
[6 empty] | CONDUIT SIZING: | STANDARD SIZING
REVISION #: | P1 |  |  |  |  | STREET:
REVISION DRAWER'S INITIALS: | [5 empty] | MAIN BREAKER LOCATION:
REVISION DATE: |  |  | P1 | ISSUED TO TOWNSHIP FOR PERMIT |  | INVERTER LOCATION: | OUTSIDE
|  |  | NO. | DESCRIPTION | DATE

## SMALL TABLES (hidden)
ONELINE TITLE BLOCK 1 |  |  |  | ONELINE TITLE BLOCK 2 |  |  |  | NEW LAYOUT TITLE BLOCK |  |  |  | EQUIPMENT SCHEDULE
|  | NODATE |  | ELECTRICAL 3 LINE DIAGRAM 0kW PV SYSTEM 0 - 0 |  |  | ELECTRICAL 3 LINE DIAGRAM |  |  |  |  | 0 | 0
|  | 0 |  |  |  | TRINITY ACCOUNT #: 0 | 0kW PV SYSTEM
P1 | [6 empty] | 0 - 0
[8 empty] | P1 | ISSUED TO TOWNSHIP FOR PERMIT
[8 empty] | NO. | DESCRIPTION |  | DATE
INVERTER 1 SPEC | [5 empty] | MODULE STRINGING SPEC | MICROINVERTER TOP LEFT TITLE BLOCK
INVERTER #1 - 0 | [5 empty] | #VALUE! | SOLAR MODULES MOUNTED TO ROOF ON 0 ARRAYS 0 - 0W MODULES 0 - ENPHASE 0 (M215-60-2LL-S22/S23)
DC |  | AC |  |  |  | *TERMINATED INSIDE INVERTER 1 |  | TRINITY ACCT #: 0
Imp | #VALUE! | Pout |  |  |  | *TERMINATED INSIDE INVERTER 2 | 0 MODULES ON 0 ENPHASE 0
Vmp | #VALUE! | Imax | 0 |  |  | *TERMINATED INSIDE INVERTER 3
Voc | #VALUE! | OCPDmin | 0 |  |  | *TERMINATED INSIDE INVERTER 4 | 0 MODULES ON 0 ENPHASE 0
Isc | #VALUE! | Vnom | 240 |  |  | *TERMINATED INSIDE INVERTER 5 |  | PROPOSED PV SOLAR SYSTEM
0 MODULES ON 0 ENPHASE 0
INVERTER 2 SPEC | [7 empty] | DRAWING DATE: |  | NODATE
INVERTER #2 - 0 | [6 empty] | 0 MODULES ON 0 ENPHASE 0 | DRAWN BY: |  | 0
DC |  | AC | [5 empty] | REVISED BY:
Imp | #VALUE! | Pout |  |  |  |  | 0 MODULES ON 0 ENPHASE 0
Vmp | #VALUE! | Imax | 0 |  |  |  |  | DC SYSTEM SIZE: |  | 0kW
Voc | #VALUE! | OCPDmin | 0 |  |  |  |  | AC SYSTEM SIZE: |  | 0kW
Isc | #VALUE! | Vnom | 240 |  |  |  |  | TOTAL MODULE COUNT: |  | 0
MODULES USED:
INVERTER 3 SPEC | [7 empty] | MODULE SPEC #:
INVERTER #3 - 0 | [7 empty] | UTILITY COMPANY:
DC |  | AC | [5 empty] | UTILITY ACCT #:
Imp | #VALUE! | Pout | [5 empty] | UTILITY METER #:
Vmp | #VALUE! | Imax | 0 |  |  |  |  | DEAL TYPE:
Voc | #VALUE! | OCPDmin | 0
Isc | #VALUE! | Vnom | 240 |  |  |  |  | P1
INVERTER 4 SPEC | [7 empty] | IN1 | IN2 | IN3 | IN4 | IN5
INVERTER #4 - 0 | [7 empty] | 0 | 0 | 0 | 0 | 0
DC |  | AC
Imp | #VALUE! | Pout
Vmp | #VALUE! | Imax | 0
Voc | #VALUE! | OCPDmin | 0
Isc | #VALUE! | Vnom | 240
INVERTER 5 SPEC
INVERTER #5 - 0
DC |  | AC
Imp | #VALUE! | Pout
Vmp | #VALUE! | Imax | 0
Voc | #VALUE! | OCPDmin | 0
Isc | #VALUE! | Vnom | 240
MODULE SPEC
PV MODULE SPECIFICATIONS
0
Imp
Vmp
Voc
Isc
KEY TABLE | [5 empty] | SMALL KEY TABLE
A | #6 THWN-2 GEC TO EXISTING GROUND ROD |  |  |  | A | #6 THWN-2 GEC TO EXISTING GROUND ROD
B | 3/4'' CONDUIT W/ 3-#10 THWN-2, 1-#10 THWN-2 GROUND |  |  |  | B | 3/4'' CONDUIT W/ 3-#10 THWN-2, 1-#10 THWN-2 GROUND
C | #10 PV WIRE (FREE AIR) W/ #6 BARE COPPER BOND TO ARRAY |  |  |  | C | #10 PV WIRE (FREE AIR) W/ #6 BARE COPPER BOND TO ARRAY
LAYOUT TITLE BLOCK |  |  | COVER TITLE
INSTALLATION OF NEW ROOF MOUNTED PV SOLAR SYSTEM
PROPOSED PV SOLAR SYSTEM |  |  | GOOD/DELETE
GOOD
NODATE
| 0 |  | WHICH DRAWING?
NO UTILITY DISCONNECT
| N.T.S |  | 0 INVERETER(S)
0kW
| 0 |  | N
B
0
|  |  | NB0 | "-TEMPLATE CODE"
EQUIPMENT LOCATION |  |  | 0 | "-delete 2nd string?"
0 |  | OUTSIDE.
OUTSIDE.
ROOF SCHEDULE

## MODULES
LIST | MODULE | MODEL NUMBER | WATTAGE | Imp | Vmp | Voc | Isc | CALCULATED Voc
HANWHA (Q.PEAK-BLK G4.1 285) | HANWHA | Q.PEAK-BLK G4.1 285 | 285 | 8.98 | 31.73 | 38.91 | 9.56 | 44.36
TRINA 260 (TSM-260 PD05.08) | TRINA 260 | TSM-260 PD05.08 | 260 | 8.5 | 30.6 | 38.2 | 9 | 44.312
TRINA 280 (TSM-280 DD05A.05) | TRINA 280 | TSM-280 DD05A.05 | 280 | 8.84 | 31.7 | 39 | 9.35 | 44.655
TRINA 285 (TSM-285 DD05A.05) | TRINA 285 | TSM-285 DD05A.05 | 285 | 8.97 | 31.8 | 39.3 | 9.45 | 44.9985
SILFAB SOLAR (SLA280M) | SILFAB SOLAR | SLA280M | 280 | 8.83 | 31.7 | 38.7 | 9.4 | 44.51
CANADIAN SOLAR 255 (CS6P-255P) | CANADIAN SOLAR 255 | CS6P-255P | 255 | 8.43 | 30.2 | 37.4 | 9 | 43.76
CANADIAN SOLAR 260 (CS6P-260P) | CANADIAN SOLAR 260 | CS6P-260P | 260 | 8.56 | 30.4 | 37.5 | 9.12 | 43.875
CANADIAN SOLAR 265 (CS6P-265P) | CANADIAN SOLAR 265 | CS6P-265P | 265 | 8.66 | 30.6 | 37.7 | 9.23 | 43.5435
LG 275 (LG275S1C-B3) | LG 275 | LG275S1C-B3 | 275 | 8.68 | 31.7 | 38.7 | 9.26 | 44.6985
LG 280 (LG280N1C-G3) | LG 280 | LG280N1C-G3 | 280 | 8.97 | 31.5 | 38.9 | 9.56 | 44.93
LG 290 (LG290N1C-G3) | LG 290 | LG290N1C-G3 | 290 | 9.19 | 31.8 | 39.2 | 9.8 | 45.28
LG 315 (LG315N1C-G4) | LG 315 | LG315N1C-G4 | 315 | 9.5 | 33.2 | 40.6 | 10.02 | 46.284
SUNPOWER 327 (SPR-327NE-WHT-D) | SUNPOWER 327 | SPR-327NE-WHT-D | 327 | 5.98 | 54.7 | 64.9 | 6.46 | 73.73
SUNEDISON 265 (F265KzD-3y) | SUNEDISON 265 | F265KzD-3y | 265 | 8.8 | 30.1 | 37.7 | 9.25 | 44.109
SUNEDSION 270 (F270KzD-3y) | SUNEDSION 270 | F270KzD-3y | 270 | 8.94 | 30.2 | 37.8 | 9.3 | 44.226
SUNIVA 270 (OPT 270-60-4-1B0) | SUNIVA 270 | OPT 270-60-4-1B0 | 270 | 8.7 | 31 | 38.4 | 9.18 | 44.832
CENTRO 280 (CM60 280) | CENTRO 280 | CM60 280 | 280 | 8.84 | 31.69 | 39.05 | 9.39 | 45.259
CENTRO 285 (CM60 285) | CENTRO 285 | CM60 285 | 285 | 8.96 | 31.81 | 39.16 | 9.49 | 45.386
CENTRO 290 (CM60 290) | CENTRO 290 | CM60 290 | 290 | 9.06 | 32.02 | 39.31 | 9.59 | 45.56
N/A
N/A
N/A
N/A
N/A
N/A

## INVERTERS
INVERTER | Pout | Iout | NO TOUCHY!!!!!! | AC WIRES (NOT MICROS) INPUTS HERE!
SE3000H-US | 3000 | 12.5 | 3/4" CONDUIT W/ 3-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4" CONDUIT W/ 3-#10 THWN-2, 1-#10 THWN-2 GROUND
SE3800H-US | 3800 | 16 | 3/4" CONDUIT W/ 3-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4" CONDUIT W/ 3-#10 THWN-2, 1-#10 THWN-2 GROUND
N/A |  |  | 0
SE3000A-US | 3000 | 12.5 | 3/4" CONDUIT W/ 3-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4" CONDUIT W/ 3-#10 THWN-2, 1-#10 THWN-2 GROUND
SE3800A-US | 3800 | 16 | 3/4" CONDUIT W/ 3-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4" CONDUIT W/ 3-#10 THWN-2, 1-#10 THWN-2 GROUND
SE5000A-US | 5000 | 21 | 3/4" CONDUIT W/ 3-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4" CONDUIT W/ 3-#10 THWN-2, 1-#10 THWN-2 GROUND
SE6000A-US | 6000 | 25 | 3/4" CONDUIT W/ 2-#8 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4" CONDUIT W/ 2-#8 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
SE7600A-US | 7600 | 32 | 3/4" CONDUIT W/ 2-#8 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4" CONDUIT W/ 2-#8 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
SE10000A-US | 10000 | 42 | 3/4" CONDUIT W/ 2-#6 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4" CONDUIT W/ 2-#6 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
SE11400A-US | 11400 | 47.5 | 3/4" CONDUIT W/ 2-#6 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4" CONDUIT W/ 2-#6 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
M215 MICROINVERTERS | 215 | 0.8959 | 0
M250 MICROINVERTERS | 250 | 1.0417 | 0
N/A |  |  | 0
N/A |  |  | 0
N/A |  |  | 0
N/A |  |  | 0
N/A |  |  | 0
N/A |  |  | 0
N/A |  |  | 0
N/A |  |  | 0
N/A |  |  | 0
N/A |  |  | 0
N/A |  |  | 0
N/A |  |  | 0
N/A |  |  | 0

## UTILITY & DEALS
UTILITY COMPANY | DEAL TYPE
EVERSOURCE | IGS
JCP&L | SUNRUN
PSE&G | SUNNOVA
ACE | CT LEASE
LIPA | SUNEDISON
CON EDISON | MOSAIC
UI | DIVIDEND
PSEG-LI | CASH
ROCKLAND ELECTRIC CO. | EFS
NAT'L GRID | FINANCE
UNITIL | SUNLIGHT
CENTRAL HUDSON G&E | MASS SOLAR LOAN
BGE
SMECO
PEPCO
DELMARVA
NYSEG
MILLTOWN ELECTRIC
VINELAND ELECTRIC

## CALCULATORS
SINGLE PHASE VOLTAGE DROP CALCULATOR |  |  | DC STRING VOLTS/AMPS CALCULATOR
VOLTAGE: |  |  | MODULE:
AMPERAGE AT END OF RUN: |  |  | # OF MODULES IN STRING:
DISTANCE OF TRENCH IN FEET: |  |  | VOLTAGE:
CONDUCTOR SIZE: | NOT AVAILABLE |  | AMPERAGE: | #REF!
REQUIRED MINIMUM CMILS: | NOT AVAILABLE
ACTUAL CMILS: | NOT AVAILABLE
EGC/NEUTRAL SIZE: | NOT AVAILABLE
VOLTS DROPPED: | NOT AVAILABLE
VD%: | NOT AVAILABLE
MINIMUM CONDUIT SIZE CALCULATOR
# OF WIRES | WIRE SIZE | DIAMETER | *(# OF WIRES)
0 |  |  | 0
NIPPLE? (12" OR LESS)
NO
EMT=
FMC=
PVC (SCHED 40)=
PVC (SCHED 80)=

## CALCULATIONS (hidden)
401925 | INVERTER 1 | INVERTER 2 | INVERTER 3 | INVERTER 4 | INVERTER 5 |  |  |  |  | INVERTER 1 | INVERTER 2 | INVERTER 3 | INVERTER 4 | INVERTER 5 | CONDUIT PICK LIST!!
INVERTER MODEL: | 0 | 0 | 0 | 0 | 0 |  |  |  | WATTAGE: | 0 | 0 | 0 | 0 | 0 | STANDARD SIZING
# OF STRINGS: | 0 | 0 | 0 | 0 | 0 | [9 empty] | 1 INCH
# OF MODULES ON LARGEST STRING: | 0 | 0 | 0 | 0 | 0
# OF MODULES ON ADDITIONAL STRING (ONLY IF DIFFERENT THAN LARGEST STRING): | 0 | 0 | 0 | 0 | 0
# OF MICROINVERTERS: | 0 | 0 | 0 | #REF! | 0 |  |  |  | SOLAR EDGE
MODULE :
MODEL #:
[6 empty] | MODULE WATTAGE: | 0
Imp:
Vmp:
MODULES: | 0 | 0 |  |  |  | Voc:
JOB NAME: | [5 empty] | Isc:
ADDRESS: | [5 empty] | CALCULATED Voc:
DATE: | NODATE
DEAL:
SERVICE AMPERAGE: | 0
TRINITY ACCOUNT #: | 0
UTILITY COMPANY: | 0
UTILITY ACCOUNT #: | 0
UTILITY METER #: | 0
DRAWER'S INITIALS: | 0
REVISION #: | P1
REVISION DRAWER'S INITIALS: | 0
REVISION DATE: |  |  | TAPS OR BREAKER:
SYSTEM SIZE: |  |  | # OF ARRAYS: | 0 |  |  | TOTAL MICRO STRINGS: | 0
| INVERTER 1 | INVERTER 2 | INVERTER 3 | INVERTER 4 | INVERTER 5 |  | TOTAL MICROINVERTERS: | 0
| 0 | 0 | 0 | 0 | 0 |  | CIRCUIT 1: | 0
Imp: | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | CIRCUIT 2: | 0
Vmp: | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | CIRCUIT 3: | 0
Voc: | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | CIRCUIT 4: | 0
Isc: | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | CIRCUIT 5: | 0
Iout: | 0 | 0 | 0 | 0 | 0
SYSTEM SIZE: | 0 | W | 0 | kW
TOTAL AMPERAGE: | 0
MAIN BREAKER/FUSE SIZE: | [9 empty] | INVERTER 1 | INVERTER 2 | INVERTER 3 | INVERTER 4 | INVERTER 5
SE?: | [8 empty] | SE MAX IMP:
SE ADC MAX: | #VALUE!
| INVERTER 1 | INVERTER 2 | INVERTER 3 | INVERTER 4 | INVERTER 5 |  | ONLY PVP's?
STRING 1: | [6 empty] | NEW SMA's?
STRING 2: | [6 empty] | ONLY MICRO's?
[7 empty] | MICROS? | NO
[7 empty] | MODEL? | 0
KEY TABLE: | 1 | #6 THWN-2 GEC TO EXISTING GROUND ROD | 1
| 2 | 3/4'' CONDUIT W/ 3-#10 THWN-2, 1-#10 THWN-2 GROUND | 2
3
4
5
6
7
8
9
10
| 11 | #10 PV WIRE (FREE AIR) W/ #6 BARE COPPER BOND TO ARRAY | 11
12
13
14
15
DC WIRE: | 0 | #10
MATERIAL LIST: | 1 | 0 | 1 | 0 |  |  | SUBPANEL OUTSIDE?: | YES
| 2 |  |  | 1 |  |  | MODULES PORTRAIT: | 0
| 3 |  |  | 1 |  |  | MODULES LANDSCAPE: | 0
| 4 |  |  | 1 |  |  | RAIL LENGTH: | 0
| 5 |  |  | 1 |  |  | ROUNDED UP: | 20
| 6 |  |  | 1 |  |  | FULL RAILS: | 2
| 7 |  |  | 0
| 8 |  |  | 1
| 9 | 2p0A BACKFEED BREAKER | 9 | 1
| 10 |  |  | 1
| 11 |  |  | 1
| 12 |  |  | 1
| 13 |  |  | 1
| 14 |  |  | 1
| 15 |  |  | 1
| 16 |  |  | 1
| 17 |  |  | 1
| 18 |  |  | 1
| 19 |  |  | 1
| 20 | METER AND METER PAN | 20 | 1
| 21 |  |  | 1
| 22 | SOLADECK BOX(ES) & HAYCO CONNECTOR(S) | 22 | 0
| 23 | 14' SECTIONS OF RAIL | 23 | 2
| 24 |  |  | 2
| 25 | FLASHINGS | 25 | 0
| 26 | CASE(S) OF BLACK SPRAY PAINT | 26 | 1
| 27 | CASE(S) OF TAR | 27 | 1
28
| 29 | PV LEAD WIRE | 29 | 0'
| 30 |  |  | ___
| 31 |  |  | ___
| 32 |  |  | ___
| 33 | T-BOLTS | 33 | ___
| 34 | MID CLIPS | 34 | ___
| 35 | END CLIPS | 35 | ___
| 36 | SPLICE KITS | 36 | ___
| 37 | GROUND LUGS | 37 | ___
| 38 |  |  | ___
| 39 |  |  | ___
| 40 |  |  | ___
| 41 |  |  | ___
| 42 |  |  | ___
VOLTAGE DROP
VOLTAGE: | NOT AVAILABLE
AMPERAGE: | NOT AVAILABLE
DISTANCE: | 40
CMILS: | #VALUE!
CONDUCTOR SIZE: | #VALUE! | #VALUE! | #VALUE!
EGC/NEUTRAL SIZE: | #VALUE!
VOLTS DROPPED: | #VALUE!
VD%: | #VALUE!

## LARGE TABLE (hidden)
MAIN BREAKER/FUSE: | 0
MAIN DISCONNECT: | 60
SERVICE AMPERAGE: | 0
UTILITY DISCO AMPERAGE: | 30
SUBPANEL AMPERAGE: | 100
INV 1 BREAKER: | 20
INV 2 BREAKER: | 20
INV 3 BREAKER: | 20
INV 4 BREAKER: | 20
INV 5 BREAKER: | 20
MICRO 1 BREAKER: | 0
MICRO 2 BREAKER: | 0
MICRO 3 BREAKER: | 0
MICRO 4 BREAKER: | 0
MICRO 5 BREAKER: | 0
# OF STRINGS COMBINED: | 1
DC REQUIRED CONDUCTOR AMP: | #VALUE!
DC WIRE SIZE: | 10
# OF CCC: | 0
DERATE %: | 1
DC CONDUCTOR AMP: | 40
DERATED CONDUCTOR AMP: | 38.4
TOTAL INVERTER AMP: | 0
^ * 1.25: | 0
AC WIRE SIZE: | 10
AC CONDUCTOR AMP: | 40
MODULE ISC OR SE 15A:
MULTIPLY ^ BY: | 1.56
PEAK TO GROUND(FT): | 0
PEAK TO GROUND(IN): | 0
R1 ORIENT: | 0
PITCH: | 0
R2 ORIENT: | 0
PITCH: | 0
R3 ORIENT: | 0
PITCH: | 0
R4 ORIENT: | 0
PITCH: | 0
STREET:
unfusedDiscoPartNum | DU221RB

## MATERIAL LIST (hidden)
JOB NAME:
ADDRESS:
| 2 ESTIMATED MAN HOURS | 0.08 DAYS (3 MEN) | 0.06 DAYS (4 MEN) | 0.04 DAYS (6 MEN)
• | 0 's (0KW)
• | NO PIPES OR VENTS BEINGS RELOCATED OR REMOVED
• | 0 INVERTERS INSTALLED OUTSIDE
• | NO TRENCH
|  | ESTIMATED | SENT TO JOB | USED
□ | 0 | 0 | ___ | ___
□ | 2p0A BACKFEED BREAKER | 1 | ___ | ___
□ | METER AND METER PAN | 1 | ___ | ___
□ | SOLADECK BOX(ES) & HAYCO CONNECTOR(S) | 0 | ___ | ___
□ | 14' SECTIONS OF RAIL | 2 | ___ | ___
□ | FLASHINGS | 0 | ___ | ___
□ | CASE(S) OF BLACK SPRAY PAINT | 1 | ___ | ___
□ | CASE(S) OF TAR | 1 | ___ | ___
□ | PV LEAD WIRE | 0' | ___ | ___
□ | T-BOLTS | ___ | ___ | ___
□ | MID CLIPS | ___ | ___ | ___
□ | END CLIPS | ___ | ___ | ___
□ | SPLICE KITS | ___ | ___ | ___
□ | GROUND LUGS | ___ | ___ | ___
^^^

## Sheet1 (hidden)
2 | Man hours |  |  | 0.04 | Days with 6 men
|  |  |  | 0.06 | Days with 4 men
|  |  |  | 0.08 | Days with 3 men
Install Size (kw) |  | 0 |  | 2 | man hours |  |  | 0
Stories |  | 1 |  | 0 | man hours added |  |  | 0
Roof Pitch |  | 0 |  | 0 | man hours added |  |  | 0
Inverter location |  |  |  | 0 | man hours added |  |  | 0
Conduit location |  | attic |  | 0 | man hours added
# of Arrays |  | 0 |  | 0 | man hours added
# of Vent pipes |  | 0 |  | 0 | man hours added
Standard Sheathing |  |  |  | 0 | man hours added
Trenching ft |  | 0 |  | 0 | man hours added
Assumptions
10kw or less, ranch, less than 35 degree pitch, inverter outside, conduit outside, 1 array, no existing vents to move, Standard sheathing
Standard install |  | 48 | man hours per 10kw standard install |  |  | 208.3333 | Watts per man hour
2 story house |  | 2 | man hours per 10kw install per story adder |  |  | 0.2 | man hours per kilowatt, per story
>35 degree pitch |  | 12 | man hours per 10kw install over 35 degrees adder |  |  | 1.2 | man hours per kilowatt, per degree
inverter inside |  | 2 | man hours per 10kw install adder |  |  | 0.2 | man hours per kilowatt
Conduit though attic |  | 2 | man hours per 10kw install adder |  |  | 0.2 | man hours per kilowatt
multiple arrays |  | 1 | man hours per 10kw install per array adder |  |  | 0.1 | man hours per kilowatt, per array
Vent pipes |  | 1 | man hours per 10kw install per vent pipe adder |  |  | 0.1 | man hours per kilowatt, per vent pipe
Non-standard Sheathing |  | 32 | man hours per 10kw install adder |  |  | 3.2 | man hours per kilowatt
Trenching ft |  | 0.083 | man hours per ft |  |  | 0.083 | man hours per ft