## Dropdown Master
Your title here….. | [13 empty] | 600 | 2 | TS480 | 8000 | 0.98 | 200
|  |  | Key |  | Scale | [8 empty] | 1000 | 4 | TS208 | 5750 | 0.975 | 200
|  |  | User Input |  |  |  |  | Min Vmppt |  |  | Min Temp Voc
|  |  | Listed choices |  |  |  | <100% | 100-110% | >110% | <90% | 90-100% | >100%
[5 empty] | Voltage Scale |  | <-------¦ | <--------------> | ¦<------------- | ------------->¦ | <-------------> | ¦--------->
[8 empty] | Low | Great |  | Be careful | NEC no go…
Module Input Data
Module Name | Suniva 275W | <<<< |  |  |  |  | <80% | 80-90% | 90-125% | 125-150% | >150%
V Temp Coeff (%) | -0.335% |  |  |  | Power Scale |  | <-------¦ | <--------------> | <--------------> | <--------------> | ¦--------->
Module Power (STC, W) | 275 | [5 empty] | Ok, but underpowered…. |  | Great
Voc (V) | 38.6
Vmppt (V) | 31.5 |  |  | Notes
Imppt (A) | 8.74 |  |  | > Should not exceed Min Temp Voc maximum voltage (either 600 or 1,000V)
Cell T Rise (°C) | 20 |  |  | > Change String Length Input Cell to be under Min-Temp Voc limit, make sure inverter power level and other parameters look good
(Note Min Vmppt is 425V: Above this unit will give full power, but unit will still track down to 200V or below)
String Length Input | 18
System |  |  |  | TrueString String Length Calculator
Max Voc (V) | 1000
[5 empty] | String Length: | 15 | 16 | 17 | 18 | 19 | 20 | 21
Ambient Temperature Assumptions |  |  |  | Min Temp | Voc (V) | 646.8877 | 690.0136 | 733.1395 | 776.2653 | 819.3912 | 862.517 | 905.6428 | V
Min Temp (°C) | -10 |  |  | Min Temp | Vmppt (V) | 496.2431 | 529.326 | 562.4089 | 595.4918 | 628.5746 | 661.6575 | 694.7404 | V
Max Temp (°C) | 45 |  |  |  | Pdc (W) | 8674.3298 | 9252.6185 | 9830.9071 | 10409.1958 | 10987.4844 | 11565.7731 | 12144.0618 | W
Nominal Temp (°C) | 25 |  |  |  | Pac (W) | 8500.8432 | 9067.5661 | 9634.289 | 10201.0119 | 10767.7348 | 11334.4576 | 11901.1805 | W
|  |  |  | Nom Temp | Vmppt (V) | 440.8425 | 470.232 | 499.6215 | 529.011 | 558.4005 | 587.79 | 617.1795 | V
TrueString Inverter Input Data |  |  |  |  | Pdc (W) | 7705.9269 | 8219.6554 | 8733.3838 | 9247.1123 | 9760.8407 | 10274.5692 | 10788.2977 | W
Model | TS480 |  |  |  | Pac (W) | 7551.8084 | 8055.2623 | 8558.7161 | 9062.17 | 9565.6239 | 10069.0778 | 10572.5317 | W
Power Rating (W) | 8000 |  |  | Max Temp | Vmppt (V) | 409.185 | 436.464 | 463.743 | 491.022 | 518.301 | 545.58 | 572.859 | V
Average Efficiency (%) | 98% |  |  |  | Pdc (W) | 7152.5538 | 7629.3907 | 8106.2276 | 8583.0646 | 9059.9015 | 9536.7384 | 10013.5753 | W
# Strings | 2 |  |  |  | Pac (W) | 7009.5027 | 7476.8029 | 7944.1031 | 8411.4033 | 8878.7035 | 9346.0036 | 9813.3038 | W
Min Vmppt (V) | 200 |  |  | STC Stacking Ratio |  | 103.1% | 110% | 116.9% | 123.8% | 130.6% | 137.5% | 144.4%
HiQ Solar, Inc. v3.0, July 2015 |  |  |  | Use at own risk, HiQ Solar, Inc. accepts no responsibility for errors, omissions, etc.
www.hiqsolar.com | [12 empty] | Rugged Solar Inverters for Commercial 3-Phase Installations
Note on G5: Scale of % Vmppt to % Voc range
Note on C8: Guy Foster: Dropdown, driven from "Module Table" tab
Note on G9: Power scale compared to inverter nominal output power
Note on B14: Usually difference between Normal Cell Operating Temperature (NOCT) and STC temperature
Note on F18: Calculations are based on STC. Temperature derating applied to voltage but not current values. Powers calculated from Vmppt (temp derated) and Imp (not derated). Tool gives order of magnitude guidance but is not a substitute for a system design tool.
Note on B28: Input cells populated with correct info for HiQ Solar TrueString inverter
Note on F31: STC module power vs. inverter nominal power rating

## Your Module Table
Module Name | Model # | V Temp Coeff (%) | Module Power (STC, W) | Voc (V) | Vmppt (V) | Imppt (A) | Cell T Rise (°C)
BenQ 96 cell 333W | PM096B00 | -0.26% | 333 | 64.9 | 54.7 | 6.09 | 20
Canadian Solar 295W | CS6X-295P | -0.34% | 295 | 44.5 | 36 | 8.19 | 20
Canadian Solar 310W | CS6X-305P | -0.34% | 310 | 44.9 | 36.4 | 8.52 | 20 | 'Vlookup' list that drives "Dropdown Master" tab.
ET Solar 305W | ET-P672305WW | -0.34% | 305 | 45.12 | 37.18 | 8.21 | 20 | Feel free to add your own modules to the list as needed
Heliene 305W | 72M305 | -0.32% | 305 | 45.1 | 36.65 | 8.32 | 20
Hyundai 300W | HiS-S300MI | -0.334% | 300 | 45.4 | 37.4 | 8 | 20
LG 305W | LG305N1C-B3 | -0.29% | 305 | 40 | 32.1 | 9.52 | 20
SolarWorld 270W | SW270 Mono | -0.3% | 270 | 39.2 | 30.9 | 8.81 | 20
Stion 150W | STL-150A (CIGS module) | -0.24% | 150 | 80.8 | 62.7 | 2.39 | 20
Suniva 275W | OPT275-60-4-1B0 | -0.335% | 275 | 38.6 | 31.5 | 8.74 | 20
Suniva 325W | OPT 325-72-4-100-BAA | -0.335% | 325 | 46.4 | 37.1 | 8.76 | 20
Suniva 330W | OPT 330-72-4-100 | -0.34% | 330 | 46.5 | 37.5 | 8.8 | 20
SunPower 327W | (- COM is 1,000V model) | -0.32% | 327 | 64.9 | 54.7 | 5.98 | 20
SunPower 345W |  | -0.32% | 345 | 68.2 | 57.3 | 6.02 | 20
Sunpreme 360W | Maxima GXB 360W | -0.27% | 360 | 52.2 | 42.4 | 8.5 | 20
Sunpreme 370W | SNPM-GxB-370 | -0.28% | 370 | 54.7 | 42.5 | 8.7 | 20
Trina 240W | TSM-240PA05 | -0.35% | 240 | 37.2 | 30.4 | 7.89 | 20
Trina 250W | TSM-250PA05 | -0.32% | 250 | 37.6 | 30.3 | 8.26 | 20
Yingli 245W | YL245P-29b | -0.33% | 245 | 37.8 | 30.2 | 8.11 | 20
Yingli 295W | YL295P-35b | -0.33% | 295 | 45.4 | 36.3 | 8.12 | 20
Note on H1: Usually difference between Normal Cell Operating Temperature (NOCT) and STC temperature