## FORM
MODULE TYPE: | HANWHA 315 (Q.PEAK DUO BLK-G5 315)
MAX MODULES PER STRING: | 18
MAX MODULES: | 21 |  |  |  | (USE 5 FOR MICROS)
| INVERTER 1 | INVERTER 2 | INVERTER 3 | INVERTER 4 | INVERTER 5
INVERTER MODEL: | SE5000H-US |  |  |  |  | M250
# OF STRINGS: | 2
STRING #1: | 11
STRING #2: | 10
STRING #3:
MODULE COUNT: | 21 |  |  | # OF MICROINVERTERS:
↓ CHECK ALERT WINDOW! ↓ | 133% |  |  |  |  | ↓ CHECK ALERT WINDOW! ↓
JOB NAME: | Klein, Jed- |  | LINE TAPS OR BREAKER: | LINE TAPS | USE LINE TAPS |  | INV PN: | 000BNC4 - APP NO SCREEN
ADDRESS 1: | 73 Newbury Rd |  | STATE?: | NJ
ADDRESS 2: | Howell, NJ 07731
LAT AND LONG: | 40.147226,-74.212281
DATE: | 2019-08-14 |  | INVERTER/SUBPANEL OUTSIDE?: | YES |  |  |  | PLEASE CHECK ROOFS PAGE!!
DEAL: | SUNNOVA |  | HOW MANY MODULES ARE LANDSCAPED?: | 1 |  |  | PEAK TO GROUND: | 16 | FEET
TRINITY ACCOUNT #: | 2019-07-362193 |  | ROOF MOUNT OR GROUND MOUNT?: | ROOF MOUNT |  |  |  | 7 | INCHES
MAIN BREAKER AMPERAGE: | 100 |  | TRENCH?: |  |  |  | R1 ORIENTATION: |  | °
MAIN BUSBAR AMPERAGE: | 100 | [5 empty] | PITCH: |  | °
UTILITY COMPANY: | JCP&L | [5 empty] | R2 ORIENTATION: |  | °
UTILITY ACCOUNT #: | 100079182075 | [5 empty] | PITCH: |  | °
UTILITY METER #: | S41155128 |  | BACKFEED BREAKER TYPE: | UNKOWN BRAND |  |  | R3 ORIENTATION: |  | °
RACKING: | OTHER |  | IS JOB CLOSE TO SALT WATER?: | NO |  |  | PITCH: |  | °
DRAWER'S INITIALS: | RF | NO LONGER A NOOB | STANDARD SHEATHING?: | YES |  |  | R4 ORIENTATION: |  | °
# OF ARRAYS: | 2 |  |  | ISSUED/REVISIONS |  |  | PITCH: |  | °
AHJ: | Howell Township, NJ | [5 empty] | CONDUIT SIZING: | STANDARD SIZING
REVISION #: | A1 | [5 empty] | STREET: | Newbury Rd
REVISION DRAWER'S INITIALS: | JMS | KAMEHAMEHA! | A1 | AS BUILT | 2019-09-19 |  | MAIN BREAKER LOCATION: | INSIDE
REVISION DATE: | 2019-09-19 |  | P1 | ISSUED TO TOWNSHIP FOR PERMIT | 2019-08-14 |  | DISCONNECT LOCATION: | SAME AS ABOVE
|  |  | NO. | DESCRIPTION | DATE |  | INVERTER LOCATION: | OUTSIDE
SUNNOVA OVER 125%!

## MODULES
LIST | MODULE | MODEL NUMBER | WATTAGE | Imp | Vmp | Voc | Isc | CALCULATED Voc
HANWHA 315 (Q.PEAK DUO BLK-G5 315) | HANWHA 315 | Q.PEAK DUO BLK-G5 315 | 315 | 9.41 | 33.46 | 40.29 | 9.89 | 45.93
HANWHA 300 (HLS72P6-PB-1-300) | HANWHA 300 | HLS72P6-PB-1-300 | 300 | 8.32 | 36.1 | 44.9 | 8.78 | 48.279
HANWHA 295 (Q.PEAK-BLK G4.1 295) | HANWHA 295 | Q.PEAK-BLK G4.1 295 | 295 | 9.17 | 32.19 | 39.48 | 9.7 | 45.0072
HANWHA 290 (Q.PEAK-BLK G4.1 290) | HANWHA 290 | Q.PEAK-BLK G4.1 290 | 290 | 9.07 | 31.96 | 39.19 | 9.63 | 44.6766
HANWHA 285 (Q.PEAK-BLK G4.1 285) | HANWHA 285 | Q.PEAK-BLK G4.1 285 | 285 | 8.98 | 31.73 | 38.91 | 9.56 | 44.36
TRINA 290 (TSM-290 DD05A.05) | TRINA 290 | TSM-290 DD05A.05 | 290 | 9.01 | 32.2 | 39.5 | 9.5 | 45.2275
TRINA 295 (TSM-295 DD05A.05) | TRINA 295 | TSM-295 DD05A.05 | 295 | 9.08 | 32.5 | 39.7 | 9.55 | 45.4565
TRINA 300 (TSM-300 DD05A.05) | TRINA 300 | TSM-300 DD05A.05 | 300 | 9.19 | 32.6 | 39.8 | 9.77 | 45.571
LG 310 (LG310N1C-G4) | LG 310 | LG310N1C-G4 | 310 | 9.45 | 32.8 | 40.4 | 9.96 | 46.056
LG 325 (LG325N1C-A5) | LG 325 | LG325N1C-A5 | 325 | 9.77 | 33.3 | 40.8 | 10.41 | 46.308
LG 330 (LG330N1C-A5) | LG 330 | LG330N1C-A5 | 330 | 9.8 | 33.7 | 40.9 | 10.45 | 46.42
LG 335 (LG335N1C-A5) | LG 335 | LG335N1C-A5 | 335 | 9.83 | 34.1 | 41 | 10.49 | 46.535
HANWHA 315 (Q.PEAK DUO BLK-G5 315) | HANWHA 315 | Q.PEAK DUO BLK-G5 315 | 315 | 9.41 | 33.46 | 40.29 | 9.89 | 45.93
HANWHA 310 (Q.PEAK DUO BLK-G5 310) | HANWHA 310 | Q.PEAK DUO BLK-G5 310 | 310 | 9.36 | 33.12 | 40.02 | 9.83 | 45.6228
N/A
N/A
N/A
N/A
N/A
N/A
N/A
RECOM 290 (RCM-290-6MB) | RECOM 290 | RCM-290-6MB | 290 | 8.86 | 32.7 | 39.9 | 9.75 | 46.284
JINKO 280 (JKM280M-60B) | JINKO 280 | JKM280M-60B | 280 | 8.81 | 31.8 | 38.6 | 9.49 | 44.197
JINKO 285 (JKM285M-60B) | JINKO 285 | JKM285M-60B | 285 | 8.9 | 32 | 38.7 | 9.51 | 44.3315
JINKO 290 (JKM290M-60B) | JINKO 290 | JKM290M-60B | 290 | 9.02 | 32.2 | 39.5 | 9.61 | 45.2275
SILFAB SOLAR (SLA285M) | SILFAB SOLAR | SLA285M | 285 | 8.91 | 32 | 39.1 | 9.47 | 44.965
CONGA CODE
Hanwha - Q.PEAK DUO BLK-G5 315

## INVERTERS
INVERTER | Pout | Iout | NO TOUCHY!!!!!! | AC WIRES (NOT MICROS) INPUTS HERE!
SE3000H-US | 3000 | 12.5 | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
SE3800H-US | 3800 | 16 | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
SE5000H-US | 5000 | 21 | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
SE6000H-US | 6000 | 25 | 3/4'' CONDUIT W/ 2-#8 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4'' CONDUIT W/ 2-#8 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
SE7600H-US | 7600 | 32 | 3/4'' CONDUIT W/ 2-#8 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4'' CONDUIT W/ 2-#8 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
SE10000H-US | 10000 | 42 | 3/4'' CONDUIT W/ 2-#6 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4'' CONDUIT W/ 2-#6 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
SE11400H-US | 11400 | 47.5 | 3/4'' CONDUIT W/ 2-#6 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4'' CONDUIT W/ 2-#6 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
N/A
SE3000A-US | 3000 | 12.5 | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
SE3800A-US | 3800 | 16 | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
SE5000A-US | 5000 | 21 | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
SE6000A-US | 6000 | 25 | 3/4'' CONDUIT W/ 2-#8 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4'' CONDUIT W/ 2-#8 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
SE7600A-US | 7600 | 32 | 3/4'' CONDUIT W/ 2-#8 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4'' CONDUIT W/ 2-#8 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
SE10000A-US | 10000 | 42 | 3/4'' CONDUIT W/ 2-#6 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4'' CONDUIT W/ 2-#6 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
SE11400A-US | 11400 | 47.5 | 3/4'' CONDUIT W/ 2-#6 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 3/4'' CONDUIT W/ 2-#6 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
M215 MICROINVERTERS | 215 | 0.8959 | 0
M250 MICROINVERTERS | 250 | 1.0417 | 0
IQ6 MICROINVERTERS | 230 | 0.9583 | 0
IQ6PLUS MICROINVERTERS | 280 | 1.1667 | 0
IQ7 MICROINVERTERS | 240 | 0.9583 | 0
IQ7PLUS MICROINVERTERS | 290 | 1.1667 | 0
N/A |  |  | 0
N/A |  |  | 0
N/A |  |  | 0
N/A |  |  | 0
N/A |  |  | 0
N/A |  |  | 0
N/A |  |  | 0

## UTILITY, DEALS & STATE
UTILITY COMPANY | DEAL TYPE | STATE
JCP&L | Sunnova | NJ
JCP&L | SUNNOVA | NJ
EVERSOURCE | IGS | NJ
JCP&L | SUNRUN | NY
PSE&G | SUNNOVA | CT
ACE | CT LEASE | MA
LIPA | SUNEDISON | MD
CON EDISON | MOSAIC | RI
UI | DIVIDEND | PA
PSEG-LI | CASH | DE
ROCKLAND ELECTRIC CO. | EFS
NAT'L GRID | FINANCE
UNITIL | SUNLIGHT
CENTRAL HUDSON G&E | MASS SOLAR LOAN
BGE
SMECO
PEPCO
DELMARVA
NYSEG
MILLTOWN ELECTRIC
VINELAND ELECTRIC
PPL
MET ED

## MATERIAL LIST
JOB NAME: | KLEIN, JED-
ADDRESS: | 73 Newbury Rd Howell, NJ 07731 40.147226,-74.212281
| 36.398 ESTIMATED MAN HOURS | 1.52 DAYS (3 MEN) | 1.14 DAYS (4 MEN) | 0.76 DAYS (6 MEN)
• | 21 HANWHA 315's (6.615KW)
• | 2 SEPARATE ARRAYS
• | 16' PEAK TO GROUND
• | 20 PORTRAIT & 1 LANDSCAPED
• | NO PIPES OR VENTS BEINGS RELOCATED OR REMOVED
• | 1 INVERTERS INSTALLED OUTSIDE
• | NO TRENCH
|  | ESTIMATED | SENT TO JOB | USED
□ | HANWHA 315 (Q.PEAK DUO BLK-G5 315) --- P320 SE OPTIMIZERS | 21 | ___ | ___
□ | SE5000H-US000BNC4 | 1 | ___ | ___
□ | 60A INDOOR FUSED DISCONNECT W/ (2) 30A FUSES | 1 | ___ | ___
□ | SOLADECK BOX(ES) & HAYCO CONNECTOR(S) | 2 | ___ | ___
□ | 14' SECTIONS OF RAIL | 13 | ___ | ___
□ | INSULATED BUG BITES (LINE TAPS) | 2 | ___ | ___
□ | FLASHINGS | 42 | ___ | ___
□ | CASE(S) OF BLACK SPRAY PAINT | 1 | ___ | ___
□ | CASE(S) OF TAR | 1 | ___ | ___
□ | PV LEAD WIRE | 100' | ___ | ___
□ | T-BOLTS | ___ | ___ | ___
□ | MID CLIPS | ___ | ___ | ___
□ | END CLIPS | ___ | ___ | ___
□ | SPLICE KITS | ___ | ___ | ___
□ | GROUND LUGS | ___ | ___ | ___
^^^

## CURRENT EXCEL ROOFS
CONGA CODES
ROOF ORIENTATION |  | ROOF PITCH |  | ROOF HEIGHT | Randy Faiges |  | NUMBER OF MODULES PER ROOF | ROOF PITCH | ROOF ORIENTATION | 16 | 7
1 | 15 | 1 | 18 | 16 |  | Roof 1 | 0 | 18 | 15
| 195 |  | 18 |  |  | Roof 2 | 16 | 19 | 195
| 15 |  | 18 |  |  | Roof 3 | 0 | 18 | 15
| 195 |  | 18 |  |  | Roof 4 | 5 | 19 | 195
| 285 |  | 14 |  |  | Roof 5 | 0 | 14 | 285
| 105 |  | 14 |  |  | Roof 6 | 0 | 14 | 105
2 |  | 2
3 |  | 3
4 |  | 4
5 |  | 5
6 |  | 6
7 |  | 7
8 |  | 8

## REVISION LIST
P1 |  |  |  | P2 |  |  |  | P3 |  |  |  | P4 |  |  |  | P5 |  |  |  | R1 |  |  |  | R2 |  |  |  | R3 |  |  |  | R4 |  |  |  | R5 |  |  |  | A1 |  |  |  | A2 |  |  |  | A3 |  |  |  | A4 |  |  |  | A5
ROOF | MODULES | PITCH | ORIENTATION | ROOF | MODULES | PITCH | ORIENTATION | ROOF | MODULES | PITCH | ORIENTATION | ROOF | MODULES | PITCH | ORIENTATION | ROOF | MODULES | PITCH | ORIENTATION | ROOF | MODULES | PITCH | ORIENTATION | ROOF | MODULES | PITCH | ORIENTATION | ROOF | MODULES | PITCH | ORIENTATION | ROOF | MODULES | PITCH | ORIENTATION | ROOF | MODULES | PITCH | ORIENTATION | ROOF | MODULES | PITCH | ORIENTATION | ROOF | MODULES | PITCH | ORIENTATION | ROOF | MODULES | PITCH | ORIENTATION | ROOF | MODULES | PITCH | ORIENTATION | ROOF | MODULES | PITCH | ORIENTATION
Roof 1 | 0 | 18 | 15 | [36 empty] | Roof 1 | 0 | 18 | 15
Roof 2 | 16 | 18 | 195 | [36 empty] | Roof 2 | 16 | 19 | 195
Roof 3 | 0 | 18 | 15 | [36 empty] | Roof 3 | 0 | 18 | 15
Roof 4 | 5 | 18 | 195 | [36 empty] | Roof 4 | 5 | 19 | 195
Roof 5 | 0 | 14 | 285 | [36 empty] | Roof 5 | 0 | 14 | 285
Roof 6 | 0 | 14 | 105 | [36 empty] | Roof 6 | 0 | 14 | 105
ELECTRICAL |  |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  |  |  | ELECTRICAL |  |  |  | ELECTRICAL
RACKING | UNIRAC SMF (RAILLESS) |  |  | RACKING |  |  |  | RACKING |  |  |  | RACKING |  |  |  | RACKING |  |  |  | RACKING |  |  |  | RACKING |  |  |  | RACKING |  |  |  | RACKING |  |  |  | RACKING |  |  |  | RACKING |  |  |  | RACKING |  |  |  | RACKING |  |  |  | RACKING |  |  |  | RACKING
MODULE TYPE | HANWHA 315 |  |  | MODULE TYPE |  |  |  | MODULE TYPE |  |  |  | MODULE TYPE |  |  |  | MODULE TYPE |  |  |  | MODULE TYPE |  |  |  | MODULE TYPE |  |  |  | MODULE TYPE |  |  |  | MODULE TYPE |  |  |  | MODULE TYPE |  |  |  | MODULE TYPE |  |  |  | MODULE TYPE |  |  |  | MODULE TYPE |  |  |  | MODULE TYPE |  |  |  | MODULE TYPE
INVERTER TYPE | SOLAR EDGE (HD WAVE) |  |  | INVERTER TYPE |  |  |  | INVERTER TYPE |  |  |  | INVERTER TYPE |  |  |  | INVERTER TYPE |  |  |  | INVERTER TYPE |  |  |  | INVERTER TYPE |  |  |  | INVERTER TYPE |  |  |  | INVERTER TYPE |  |  |  | INVERTER TYPE |  |  |  | INVERTER TYPE |  |  |  | INVERTER TYPE |  |  |  | INVERTER TYPE |  |  |  | INVERTER TYPE |  |  |  | INVERTER TYPE
INTERCONNECTION | Line Tap |  |  | INTERCONNECTION |  |  |  | INTERCONNECTION |  |  |  | INTERCONNECTION |  |  |  | INTERCONNECTION |  |  |  | INTERCONNECTION |  |  |  | INTERCONNECTION |  |  |  | INTERCONNECTION |  |  |  | INTERCONNECTION |  |  |  | INTERCONNECTION |  |  |  | INTERCONNECTION |  |  |  | INTERCONNECTION |  |  |  | INTERCONNECTION |  |  |  | INTERCONNECTION |  |  |  | INTERCONNECTION
DISCONNECT | Fused |  |  | DISCONNECT |  |  |  | DISCONNECT |  |  |  | DISCONNECT |  |  |  | DISCONNECT |  |  |  | DISCONNECT |  |  |  | DISCONNECT |  |  |  | DISCONNECT |  |  |  | DISCONNECT |  |  |  | DISCONNECT |  |  |  | DISCONNECT |  |  |  | DISCONNECT |  |  |  | DISCONNECT |  |  |  | DISCONNECT |  |  |  | DISCONNECT
PRODUCTION METER | No P Meter |  |  | PRODUCTION METER |  |  |  | PRODUCTION METER |  |  |  | PRODUCTION METER |  |  |  | PRODUCTION METER |  |  |  | PRODUCTION METER |  |  |  | PRODUCTION METER |  |  |  | PRODUCTION METER |  |  |  | PRODUCTION METER |  |  |  | PRODUCTION METER |  |  |  | PRODUCTION METER |  |  |  | PRODUCTION METER |  |  |  | PRODUCTION METER |  |  |  | PRODUCTION METER |  |  |  | PRODUCTION METER
UNFUSED | IF NEEDED |  |  | UNFUSED |  |  |  | UNFUSED |  |  |  | UNFUSED |  |  |  | UNFUSED |  |  |  | UNFUSED |  |  |  | UNFUSED |  |  |  | UNFUSED |  |  |  | UNFUSED |  |  |  | UNFUSED |  |  |  | UNFUSED |  |  |  | UNFUSED |  |  |  | UNFUSED |  |  |  | UNFUSED |  |  |  | UNFUSED
OCPD AMPERAGE | 30 |  |  | OCPD AMPERAGE |  |  |  | OCPD AMPERAGE |  |  |  | OCPD AMPERAGE |  |  |  | OCPD AMPERAGE |  |  |  | OCPD AMPERAGE |  |  |  | OCPD AMPERAGE |  |  |  | OCPD AMPERAGE |  |  |  | OCPD AMPERAGE |  |  |  | OCPD AMPERAGE |  |  |  | OCPD AMPERAGE |  |  |  | OCPD AMPERAGE |  |  |  | OCPD AMPERAGE |  |  |  | OCPD AMPERAGE |  |  |  | OCPD AMPERAGE
DC SYSTEM SIZE | 6615 |  |  | DC SYSTEM SIZE |  |  |  | DC SYSTEM SIZE |  |  |  | DC SYSTEM SIZE |  |  |  | DC SYSTEM SIZE |  |  |  | DC SYSTEM SIZE |  |  |  | DC SYSTEM SIZE |  |  |  | DC SYSTEM SIZE |  |  |  | DC SYSTEM SIZE |  |  |  | DC SYSTEM SIZE |  |  |  | DC SYSTEM SIZE |  |  |  | DC SYSTEM SIZE |  |  |  | DC SYSTEM SIZE |  |  |  | DC SYSTEM SIZE |  |  |  | DC SYSTEM SIZE
AC SYSTEM SIZE | 5000 |  |  | AC SYSTEM SIZE |  |  |  | AC SYSTEM SIZE |  |  |  | AC SYSTEM SIZE |  |  |  | AC SYSTEM SIZE |  |  |  | AC SYSTEM SIZE |  |  |  | AC SYSTEM SIZE |  |  |  | AC SYSTEM SIZE |  |  |  | AC SYSTEM SIZE |  |  |  | AC SYSTEM SIZE |  |  |  | AC SYSTEM SIZE |  |  |  | AC SYSTEM SIZE |  |  |  | AC SYSTEM SIZE |  |  |  | AC SYSTEM SIZE |  |  |  | AC SYSTEM SIZE
TOTAL PANELS | 21 |  |  | TOTAL PANELS |  |  |  | TOTAL PANELS |  |  |  | TOTAL PANELS |  |  |  | TOTAL PANELS |  |  |  | TOTAL PANELS |  |  |  | TOTAL PANELS |  |  |  | TOTAL PANELS |  |  |  | TOTAL PANELS |  |  |  | TOTAL PANELS |  |  |  | TOTAL PANELS |  |  |  | TOTAL PANELS |  |  |  | TOTAL PANELS |  |  |  | TOTAL PANELS |  |  |  | TOTAL PANELS

## CALCULATORS
SINGLE PHASE VOLTAGE DROP CALCULATOR |  |  | DC STRING VOLTS/AMPS CALCULATOR
VOLTAGE: |  |  | MODULE:
AMPERAGE AT END OF RUN: |  |  | # OF MODULES IN STRING:
DISTANCE OF TRENCH IN FEET: |  |  | VOLTAGE:
CONDUCTOR SIZE: | NOT AVAILABLE |  | AMPERAGE: | #REF!
REQUIRED MINIMUM CMILS: | NOT AVAILABLE
ACTUAL CMILS: | NOT AVAILABLE
EGC/NEUTRAL SIZE: | NOT AVAILABLE
VOLTS DROPPED: | NOT AVAILABLE
VD%: | NOT AVAILABLE
MINIMUM CONDUIT SIZE CALCULATOR
# OF WIRES | WIRE SIZE | DIAMETER | *(# OF WIRES)
2
1
1
4 |  |  | 0
NIPPLE? (12" OR LESS)
NO
EMT=
FMC=
PVC (SCHED 40)=
PVC (SCHED 80)=

## CALCULATIONS (hidden)
401925 | INVERTER 1 | INVERTER 2 | INVERTER 3 | INVERTER 4 | INVERTER 5 | [5 empty] | INVERTER 1 | INVERTER 2 | INVERTER 3 | INVERTER 4 | INVERTER 5 | CONDUIT PICK LIST!!
INVERTER MODEL: | SE5000H-US | 0 | 0 | 0 | 0 |  |  |  |  | WATTAGE: | 5000 | 0 | 0 | 0 | 0 | STANDARD SIZING
# OF STRINGS: | 2 | 0 | 0 | 0 | 0 | [5 empty] | 5000 |  |  |  |  | 1 INCH
# OF MODULES ON LARGEST STRING: | 11 | 0 | 0 | 0 | 0
# OF MODULES ON ADDITIONAL STRING (ONLY IF DIFFERENT THAN LARGEST STRING): | 10 | 0 | 0 | 0 | 0 | [10 empty] | <a href="/0013200001C1E29AAF" target="_blank">Howell Township, NJ</a>
# OF MICROINVERTERS: | 21 | 0 | 0 | #REF! | 0 |  |  |  |  | SOLAR EDGE | [5 empty] | Howell Township, NJ</a>
| 11 |  |  |  |  | MODULE : | HANWHA 315 | [8 empty] | Howell Township, NJ
| 10 |  |  |  |  | MODEL #: | Q.PEAK DUO BLK-G5 315
[6 empty] | MODULE WATTAGE: | 315 | [8 empty] | A1
[6 empty] | Imp: | 9.41
[6 empty] | Vmp: | 33.46
MODULES: | 21 | HANWHA 315 (Q.PEAK DUO BLK-G5 315) |  |  |  | Voc: | 40.29
JOB NAME: | KLEIN, JED- |  |  |  |  | Isc: | 9.89
ADDRESS: | 73 Newbury Rd Howell, NJ 07731 40.147226,-74.212281 |  |  |  |  | CALCULATED Voc: | 45.93
DATE: | 2019-08-14
DEAL: | (SUNNOVA)
SERVICE AMPERAGE: | 100
TRINITY ACCOUNT #: | 2019-07-362193
UTILITY COMPANY: | JCP&L
UTILITY ACCOUNT #: | 100079182075
UTILITY METER #: | S41155128
DRAWER'S INITIALS: | RF
REVISION #: | A1
REVISION DRAWER'S INITIALS: | JMS
REVISION DATE: | 2019-09-19 |  | TAPS OR BREAKER: | YES
SYSTEM SIZE: |  |  | # OF ARRAYS: | 2 |  |  | TOTAL MICRO STRINGS: | 0
| INVERTER 1 | INVERTER 2 | INVERTER 3 | INVERTER 4 | INVERTER 5 |  | TOTAL MICROINVERTERS: | 0
| SE5000H-US | 0 | 0 | 0 | 0 |  | CIRCUIT 1: | 0
Imp: | 13.5 | 0 | 0 | 0 | 0 |  | CIRCUIT 2: | 0
Vmp: | 380 | 0 | 0 | 0 | 0 |  | CIRCUIT 3: | 0
Voc: | 480 | 0 | 0 | 0 | 0 |  | CIRCUIT 4: | 0
Isc: | 30 | 0 | 0 | 0 | 0 |  | CIRCUIT 5: | 0
Iout: | 21 | 0 | 0 | 0 | 0
SYSTEM SIZE: | 6615 | W | 6.615 | kW
TOTAL AMPERAGE: | 26.25
MAIN BREAKER/FUSE SIZE: | 30 | [9 empty] | INVERTER 1 | INVERTER 2 | INVERTER 3 | INVERTER 4 | INVERTER 5
SE?: | YES | [8 empty] | SE MAX IMP: | 13.5
SE ADC MAX: | 9.9
| INVERTER 1 | INVERTER 2 | INVERTER 3 | INVERTER 4 | INVERTER 5 |  | ONLY PVP's?
STRING 1: | 1 STRING OF 11 MODULES IN SERIES - 380 Vmax | [5 empty] | NEW SMA's?
STRING 2: | 1 STRING OF 10 MODULES IN SERIES - 380 Vmax
STRING 3: | [6 empty] | ONLY MICRO's?
[7 empty] | MICROS? | NO
[7 empty] | MODEL? | 0
KEY TABLE: | 1 | #6 THWN-2 GEC TO EXISTING GROUND ROD | 1
| 2 | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 2
| 3 | 3/4'' CONDUIT W/ 4-#10 THWN-2, 1-#10 THWN-2 GROUND | 3 |  |  | CONDUIT DESCRIBER B
| 4 | [5 empty] | STANDARD SIZING
| 5 | 3/4'' CONDUIT W/ 4-#10 THWN-2, 1-#10 THWN-2 GROUND | 5 |  |  | STATE | NJ
| 6 |  |  |  |  | INVERTER | SE
| 7 |  |  |  |  | CONDUIT SIZE | 3/4''
| 8 | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND | 8 |  |  | HOT WIRES | 10
| 9 |  |  |  |  | NEUTRAL | 10
| 10 |  |  |  |  | GROUND | 10
11
| 12 | #10 PV WIRE (FREE AIR) W/ #6 BARE COPPER BOND TO ARRAY | 12 |  |  | MINIMUM CONDUIT SIZE CALCULATOR
| 13 | 3/4'' CONDUIT W/ 2-#6 THWN-2, 1-#6 THWN-2, 1-#8 THWN-2 GROUND | 13 |  |  | # OF WIRES | WIRE SIZE | DIAMETER | *(# OF WIRES)
| 14 |  |  |  |  | 2 | 10 | 0.0211 | 0.0422
| 15 |  |  |  |  | 1 | 10 | 0.0211 | 0.0211
[6 empty] | 1 | 10 | 0.0211 | 0.0211
DC WIRE: | 4 | #10
[6 empty] | 4 |  |  | 0.0844
|  | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND |  |  |  | EMT= | 0.5
MATERIAL LIST: | 1 | HANWHA 315 (Q.PEAK DUO BLK-G5 315) --- P320 SE OPTIMIZERS | 1 | 21 |  |  | SUBPANEL OUTSIDE?: | YES
| 2 | SE5000H-US000BNC4 | 2 | 1 |  |  | MODULES PORTRAIT: | 20
| 3 |  |  | 1 |  |  | MODULES LANDSCAPE: | 1
| 4 |  |  | 1 |  |  | RAIL LENGTH: | 161.5
| 5 |  |  | 1 |  |  | ROUNDED UP: | 180
| 6 |  |  | 1 |  |  | FULL RAILS: | 13
| 7 |  |  | 0
| 8 |  |  | 1
| 9 | 60A INDOOR FUSED DISCONNECT W/ (2) 30A FUSES | 9 | 1
| 10 |  |  | 1 |  |  | HD Inverter PN Suffix: | 000BNC4
Test | 11 |  |  | 1
| 12 |  |  | 1
| 13 |  |  | 1
| 14 |  |  | 1
| 15 |  |  | 1
| 16 |  |  | 1
| 17 |  |  | 1
| 18 |  |  | 1
| 19 |  |  | 1
| 20 |  |  | 1
| 21 |  |  | 1
| 22 | SOLADECK BOX(ES) & HAYCO CONNECTOR(S) | 22 | 2
| 23 | 14' SECTIONS OF RAIL | 23 | 13
| 24 | INSULATED BUG BITES (LINE TAPS) | 24 | 2
| 25 | FLASHINGS | 25 | 42
| 26 | CASE(S) OF BLACK SPRAY PAINT | 26 | 1
| 27 | CASE(S) OF TAR | 27 | 1
28
| 29 | PV LEAD WIRE | 29 | 100'
| 30 |  |  | ___
| 31 |  |  | ___
| 32 |  |  | ___
| 33 | T-BOLTS | 33 | ___
| 34 | MID CLIPS | 34 | ___
| 35 | END CLIPS | 35 | ___
| 36 | SPLICE KITS | 36 | ___
| 37 | GROUND LUGS | 37 | ___
| 38 |  |  | ___
| 39 |  |  | ___
| 40 |  |  | ___
| 41 |  |  | ___
| 42 |  |  | ___
VOLTAGE DROP
VOLTAGE: | NOT AVAILABLE
AMPERAGE: | NOT AVAILABLE
DISTANCE: | 30
CMILS: | #VALUE!
CONDUCTOR SIZE: | #VALUE! | #VALUE! | #VALUE!
EGC/NEUTRAL SIZE: | #VALUE!
VOLTS DROPPED: | #VALUE!
VD%: | #VALUE!
EQUIPMENT LIST
| 21 | HANWHA 315 (Q.PEAK DUO BLK-G5 315) |  | ROOF NUMBER | ROOF PITCH | ROOF ORIENTATION
| 1 | SE5000H-US000BNC4 |  | Roof1S | Roof1PS | Roof1OS
|  |  |  | Roof2S | Roof2PS | Roof2OS
|  |  |  | Roof3S | Roof3PS | Roof3OS
|  |  |  | Roof4S | Roof4PS | Roof4OS
|  |  |  | Roof5S | Roof5PS | Roof5OS
|  |  |  | Roof6S | Roof6PS | Roof6OS

## SMALL TABLES (hidden)
ONELINE TITLE BLOCK 1 |  |  |  | ONELINE TITLE BLOCK 2 |  |  |  | NEW LAYOUT TITLE BLOCK |  |  |  | EQUIPMENT SCHEDULE
100079182075 |  | 2019-08-14 |  | ELECTRICAL 3 LINE DIAGRAM 6.615kW PV SYSTEM (SUNNOVA) 21 - HANWHA 315 (Q.PEAK DUO BLK-G5 315) |  | KLEIN, JED- | ELECTRICAL 3 LINE DIAGRAM |  |  |  |  | 21 | HANWHA 315 (Q.PEAK DUO BLK-G5 315)
S41155128 |  | RF |  |  |  | 73 Newbury Rd Howell, NJ 07731 40.147226,-74.212281 TRINITY ACCOUNT #: 2019-07-362193 | 6.615kW PV SYSTEM (SUNNOVA) |  |  |  |  | 1 | SE5000H-US000BNC4
AS BUILT 1 | [6 empty] | 21 - HANWHA 315 (Q.PEAK DUO BLK-G5 315) | A1 | AS BUILT |  | 2019-09-19
2019-09-19 |  | JMS | [5 empty] | P1 | ISSUED TO TOWNSHIP FOR PERMIT |  | 2019-08-14
[8 empty] | NO. | DESCRIPTION |  | DATE
INVERTER 1 SPEC | [5 empty] | MODULE STRINGING SPEC | MICROINVERTER TOP LEFT TITLE BLOCK
INVERTER #1 - SE5000H-US000BNC4 | [5 empty] | SOLAR MODULES MOUNTED TO ROOF ON 2 ARRAYS 21 - 315W MODULES W/ 1 SOLAR EDGE P320 PER MODULE | SOLAR MODULES MOUNTED TO ROOF ON 2 ARRAYS 21 - 315W MODULES 0 - ENPHASE 0 FALSE | KLEIN, JED-
DC |  | AC |  |  |  | 1 STRING OF 11 MODULES IN SERIES - 380 Vmax 1 STRING OF 10 MODULES IN SERIES - 380 Vmax *2 STRINGS TO BE TERMINATED IN PARALLEL INSIDE INVERTER 1 |  | TRINITY ACCT #: 2019-07-362193
Imp | 13.5 | Pout | 5000 |  |  | *TERMINATED INSIDE INVERTER 2 | 0 MODULES ON 0 ENPHASE 0
Vmp | 380 | Imax | 21 |  |  | *TERMINATED INSIDE INVERTER 3 |  | 73 NEWBURY RD HOWELL, NJ 07731 40.147226,-74.212281
Voc | 480 | OCPDmin | 26.25 |  |  | *TERMINATED INSIDE INVERTER 4 | 0 MODULES ON 0 ENPHASE 0
Isc | 30 | Vnom | 240 |  |  | *TERMINATED INSIDE INVERTER 5 |  | AS BUILT PV SOLAR SYSTEM
0 MODULES ON 0 ENPHASE 0
INVERTER 2 SPEC | [7 empty] | DRAWING DATE: |  | 2019-08-14
INVERTER #2 - | [6 empty] | 0 MODULES ON 0 ENPHASE 0 | DRAWN BY: |  | RF
DC |  | AC | [5 empty] | REVISED BY: |  | JMS
Imp | 0 | Pout |  |  |  |  | 0 MODULES ON 0 ENPHASE 0
Vmp | 0 | Imax | 0 |  |  |  |  | DC SYSTEM SIZE: |  | 6.615kW
Voc | 0 | OCPDmin | 0 |  |  |  |  | AC SYSTEM SIZE: |  | 5kW
Isc | 0 | Vnom | 240 |  |  |  |  | TOTAL MODULE COUNT: |  | 21
[8 empty] | MODULES USED: |  | HANWHA 315
INVERTER 3 SPEC | [7 empty] | MODULE SPEC #: |  | Q.PEAK DUO BLK-G5 315
INVERTER #3 - | [7 empty] | UTILITY COMPANY: |  | JCP&L
DC |  | AC | [5 empty] | UTILITY ACCT #: |  | 100079182075
Imp | 0 | Pout | [5 empty] | UTILITY METER #: |  | S41155128
Vmp | 0 | Imax | 0 |  |  |  |  | DEAL TYPE: |  | SUNNOVA
Voc | 0 | OCPDmin | 0
Isc | 0 | Vnom | 240 |  |  |  |  | A1
INVERTER 4 SPEC | [7 empty] | IN1 | IN2 | IN3 | IN4 | IN5
INVERTER #4 - | [7 empty] | 5000 | 0 | 0 | 0 | 0
DC |  | AC
Imp | 0 | Pout
Vmp | 0 | Imax | 0
Voc | 0 | OCPDmin | 0
Isc | 0 | Vnom | 240
INVERTER 5 SPEC
INVERTER #5 - 0
DC |  | AC
Imp | 0 | Pout
Vmp | 0 | Imax | 0
Voc | 0 | OCPDmin | 0
Isc | 0 | Vnom | 240
MODULE SPEC
PV MODULE SPECIFICATIONS
HANWHA 315 (Q.PEAK DUO BLK-G5 315)
Imp | 9.41
Vmp | 33.46
Voc | 40.29
Isc | 9.89
KEY TABLE | [5 empty] | SMALL KEY TABLE
A | #6 THWN-2 GEC TO EXISTING GROUND ROD | G | 3/4'' CONDUIT W/ 2-#6 THWN-2, 1-#6 THWN-2, 1-#8 THWN-2 GROUND |  | A | #6 THWN-2 GEC TO EXISTING GROUND ROD
B | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND |  |  |  | B | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
C | 3/4'' CONDUIT W/ 4-#10 THWN-2, 1-#10 THWN-2 GROUND |  |  |  | C | 3/4'' CONDUIT W/ 4-#10 THWN-2, 1-#10 THWN-2 GROUND
D | 3/4'' CONDUIT W/ 4-#10 THWN-2, 1-#10 THWN-2 GROUND |  |  |  | D | 3/4'' CONDUIT W/ 4-#10 THWN-2, 1-#10 THWN-2 GROUND
E | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND |  |  |  | E | 3/4'' CONDUIT W/ 2-#10 THWN-2, 1-#10 THWN-2, 1-#10 THWN-2 GROUND
F | #10 PV WIRE (FREE AIR) W/ #6 BARE COPPER BOND TO ARRAY |  |  |  | F | #10 PV WIRE (FREE AIR) W/ #6 BARE COPPER BOND TO ARRAY
[5 empty] | G | 3/4'' CONDUIT W/ 2-#6 THWN-2, 1-#6 THWN-2, 1-#8 THWN-2 GROUND
LAYOUT TITLE BLOCK |  |  | COVER TITLE
KLEIN, JED- |  |  | INSTALLATION OF NEW ROOF MOUNTED PV SOLAR SYSTEM
73 NEWBURY RD HOWELL, NJ 07731 40.147226,-74.212281
73 Newbury Rd Howell, NJ 07731 40.147226,-74.212281
AS BUILT PV SOLAR SYSTEM |  |  | GOOD/DELETE
GOOD
2019-08-14
| RF |  | WHICH DRAWING?
UTILITY DISCONNECT
| JMS |  | LINE TAPS
| N.T.S |  | 1 INVERETER(S)
| 6.615kW |  | U
| 21 |  | L
HANWHA 315
| Q.PEAK DUO BLK-G5 315 |  | 1
JCP&L
| 100079182075 |  | UL1 | "-TEMPLATE CODE"
EQUIPMENT LOCATION |  |  | 0 | "-delete 2nd string?"
INSIDE |  | OUTSIDE.
INSIDE |  | OUTSIDE.
ROOF SCHEDULE

## LARGE TABLE (hidden)
MAIN BREAKER/FUSE: | 30
MAIN DISCONNECT: | 60
SERVICE AMPERAGE: | 100
UTILITY DISCO AMPERAGE: | 60
SUBPANEL AMPERAGE: | 100
INV 1 BREAKER: | 30
INV 2 BREAKER: | 20
INV 3 BREAKER: | 20
INV 4 BREAKER: | 20
INV 5 BREAKER: | 20
MICRO 1 BREAKER: | 0
MICRO 2 BREAKER: | 0
MICRO 3 BREAKER: | 0
MICRO 4 BREAKER: | 0
MICRO 5 BREAKER: | 0
# OF STRINGS COMBINED: | 1
DC REQUIRED CONDUCTOR AMP: | 18.75
DC WIRE SIZE: | 10
# OF CCC: | 4
DERATE %: | 0.8
DC CONDUCTOR AMP: | 40
DERATED CONDUCTOR AMP: | 30.72
TOTAL INVERTER AMP: | 21
^ * 1.25: | 26.25
AC WIRE SIZE: | 10
AC CONDUCTOR AMP: | 40
MODULE ISC OR SE 15A: | 15
MULTIPLY ^ BY: | 1.25
PEAK TO GROUND(FT): | 16
PEAK TO GROUND(IN): | 7
R1 ORIENT: | 0
PITCH: | 0
R2 ORIENT: | 0
PITCH: | 0
R3 ORIENT: | 0
PITCH: | 0
R4 ORIENT: | 0
PITCH: | 0
STREET: | NEWBURY RD
unfusedDiscoPartNum | DU222RB
Busbar Amperage | 100
fusedDiscoPartNum | D222N
NEC705.12 | D

## Sheet1 (hidden)
36.398 | Man hours |  |  | 0.76 | Days with 6 men
|  |  |  | 1.14 | Days with 4 men
|  |  |  | 1.52 | Days with 3 men
Install Size (kw) |  | 6.615 |  | 33.752 | man hours |  |  | 0
Stories |  | 1 |  | 0 | man hours added |  |  | 0
Roof Pitch |  | 0 |  | 0 | man hours added |  |  | 0
Inverter location |  |  |  | 0 | man hours added |  |  | 0
Conduit location |  | attic |  | 1.323 | man hours added
# of Arrays |  | 2 |  | 1.323 | man hours added
# of Vent pipes |  | 0 |  | 0 | man hours added
Standard Sheathing |  |  |  | 0 | man hours added
Trenching ft |  | 0 |  | 0 | man hours added
Assumptions
10kw or less, ranch, less than 35 degree pitch, inverter outside, conduit outside, 1 array, no existing vents to move, Standard sheathing
Standard install |  | 48 | man hours per 10kw standard install |  |  | 208.3333 | Watts per man hour
2 story house |  | 2 | man hours per 10kw install per story adder |  |  | 0.2 | man hours per kilowatt, per story
>35 degree pitch |  | 12 | man hours per 10kw install over 35 degrees adder |  |  | 1.2 | man hours per kilowatt, per degree
inverter inside |  | 2 | man hours per 10kw install adder |  |  | 0.2 | man hours per kilowatt
Conduit though attic |  | 2 | man hours per 10kw install adder |  |  | 0.2 | man hours per kilowatt
multiple arrays |  | 1 | man hours per 10kw install per array adder |  |  | 0.1 | man hours per kilowatt, per array
Vent pipes |  | 1 | man hours per 10kw install per vent pipe adder |  |  | 0.1 | man hours per kilowatt, per vent pipe
Non-standard Sheathing |  | 32 | man hours per 10kw install adder |  |  | 3.2 | man hours per kilowatt
Trenching ft |  | 0.083 | man hours per ft |  |  | 0.083 | man hours per ft